## Sheet1
Facility Emeregncy Power Requirements
Equipment | Life Safety | Critical Equipment | Delayed Equipment | Battery Backup | Volts | Amps | Max Watts | Run Watts | Comments
Autoclave, Tuttnauer #3870EA |  |  | √ |  | 230V | 13A | 2990W | 453W | 3 minute "Flash" x 3 OR's [2,990W / 6.6 (9 minues)= 453 W
Autoclave, Tuttnauer #2540EA |  |  | √ |  | 120V | 11.7A | 1404W | 213W | 3 minute "Flash" x 3 OR's [1,404W / 6.6 (9 minues)= 213W
Autoclave, Statim 2000 G4 |  |  | √ |  | 115V | 15A | 1450W | 440W | 6 minute "Flash" x 3 OR's [1,450W / 3.3 (18 minues)= 440W
Constellation Vision System |  |  | √ | √ | 120V | 12A | 1440W | 1440W
Evaporative Air Cooler CO30XE |  | √ |  |  | 120V | 2.4A | 288W | 288W
LenSx Laser |  |  | √ | √ | 120V | 10A | 1200W | 1200W
Haag-Streit z 2981 power supply |  |  | √ | √ | 110V | 0.36 | 40W | 40W | Includes battery Pack with 45 minutes of reserve power.
Verian Elevation Table |  |  | √ |  | 120V | 6.3A | 756W | 756W | Table only consumes power when it is being elevated, etc.
Iridex Cyclo G6 |  |  | √ |  | 120V | .8A | 96W | 96W
Iridex Occulight GL |  |  | √ |  | 90-240V |  | 350W | 350W | 90-240 VAC, 50/40 Hz < 2000 Watts in standby, <350 Watts max.
Samsung TV |  |  | √ |  | 115V | 1.5A | 170W | 170W | TV uses less power iwhen volume is lowered or muted.
Alcon 8065998307 |  |  | √ |  | 100-240V |  | 600W | 600W
Carl Zeiss Scope |  |  | √ |  | 115V | 10A | 1150W | 1150W
Verion Digital Marker |  |  | √ |  | 19V | 5.8A | 110W | 110W
Centurion Vison System |  |  | √ | √ | 230V | 6A | 1380W | 1380W
Anesthesia Machine |  | √ |  | √ | 120V | 11.4A | 1368W | 684W | Batteries are included beneath work tray.
Multi Parameter Patient Monitor |  | √ |  | √ | 120V | 1.6A | 192W | 192W | Batteries are included
CO2 Monitor |  | √ |  |  | 120V | 1A | 120W | 120W | Batteries may be included when attached to Anesthesia Machine
Bufallo Filter |  | √ |  | √ | 120V | 8.3A | 1000W | 750W | Batteries may be included.
Bair Hugger |  | √ |  |  | 120V | 9.5A | 1140W | 700W
OR Table |  | √ |  |  | 120V | 2A | 240W | 50W
Infusion Pump |  | √ |  | √ | 120V | 42VA | 75W | 42W | Batteries are included.
Suction Pump |  | √ |  |  | 120V | 2.5A | 300W | 150w | Suction Pump may be on for 30 minutes out of the hour.
Sequential Compression Device |  | √ |  | √ | 120V | 50VA | 96W | 50W | Batteries may be included.
Electro Surgical Unit |  | √ |  |  | 120V | 540VA | 540W | 405W | Used 45 minutes out of the hour. Pen type Bovie.
OR Lights (Duo) | √ | √ |  |  | 120V |  | 160W | 80W | 80W LED bulbs per Surgical Light
Defibrillator |  | √ |  | √ | 120V | 3.5A | 420W | 420W | Batteries are included.
HVAC |  | √ |  |  | 120V |  | 800W | 800W | Portable 8000BTU A/C & Dehumidifier
Recovery Suction |  | √ |  |  | 120V | 2.5A | 300W | 150w | Suction Pump may be on for 30 minutes out of the hour.
Recovery Lights | √ | √ |  |  | 120V | 1A | 120W | 120W | 120W - four overhad flourescent bulbs
Recovery Patient Monitor |  | √ |  | √ | 120V | 1.6A | 192W | 192W | Battries are included.
Hallway Lights | √ |  |  | √ | 120V | 0 | 0 | 0 | Battries are included.
Smoke Detectors | √ |  |  | √ | 120V | 0 | 0 | 0 | Battries are included.
Fire Alarms | √ |  |  | √ | 120V | 0 | 0 | 0 | Battries are included.
Exit Signs | √ |  |  | √ | 120V | 0 | 0 | 0 | Battries are included.
Total Maximum Watts | [6 empty] | 19,495W
Total Running Watts | [7 empty] | 12,681W
Total Watts with Battery Backup | [7 empty] | 6,483W