## Sheet1
Equipment | Quantity | Volts | Max Amps | Amps in O.R. Settings | RunningWatts | Run time | continuous running | Continuous Amps | Stand-By Amps | Continuous Watts | Stand-By Watts | Notes:
Anesthesia Machine | 1 | 120V | 11.4 | 5.7 | 684 | 2 | yes |  | 5.7 |  | 1368 | Anesthesia Machine includes Batteries under the work table capable of 8 hours. In addition, maximum output would require over 24 BPM. Normal BPM is 12. Includes BP and EKG Monitor. Level;III
PhacoEmulsifier | 1 | 120V | 10 | 10 | 1200 | 1 | yes | 5 |  | 1200 |  | Used For Breast Augmentations (45 min procedure)
Bair Hugger | 1 | 120V | 9.5 | 5 | 600 | 2 | yes | 5 |  | 1200 |  | Medium Heat setting 5A recommended; High heat setting 9.5A temporary.
Buffalo Filter | 1 | 120V | 10 | 6.2 | 746 | 2 | yes |  | 6.2 |  | 1492 | 746W or 1 HP Smoke/Gas Evacuator; Specs attached. For Level III
CO2 Machine | 1 | 120V | 5 | 1 | 100 | 2 | yes |  | 1 |  | 200 | Measures CO2 expiration, includes condenser for sampling line. Confirms intubation. For General Anesthesia. Level III
OR Table | 1 | 120V | 2 | 2 | 240 | 0.25 | no | 2 |  |  | 60 | Used for trendelenburg and/or lifting the HOB.
Infusion Pump | 1 | 120V | 4 | 1.6 | 75 | 0.5 | no |  | 1.6 |  | 37.5 | Used for IV Sedation to administer profol. Not routinely used. At sedation setting equals 75 W
RM 2000V Anesthesia Suction Pump | 1 | 120V | 12 | 6 | 720 | 0.25 | no |  | 6 |  | 180 | suction setting is 15MM/HG for throat and nasal suctioning. For Level III
Yag Laser | 1 | 240V | 15 | 7 | 1680 | 0.5 | no |  | 7 |  | 1680 | 30 Minute procedure
SCD (Sequential Compression Device) | 1 | 120V | 0.8 | 0.8 | 96 | 2 | yes | 0.8 |  | 192 |  | Compression device for legs, Squeezes legs with air evry 30 seconds.
Electro Surgical Unit | 1 | 120V | 9 | 2.25 | 270 | 2 | no | 2.25 |  |  | 540 | Cautery used to stop bleeding as necessary
Ceiling Lights |  | 120V | 12 | 12 | 1440 | 2 | yes | 12 |  | 2880
Defibrillator | 1 | 120V | 3.5 | 3.5 | 420 | 0.25 | no |  | 3.5 |  | 105 | Used during Code Blue 360 Joules per shock
HVAC (8,000 BTU) | 1 | 120V | 6.6 |  | 800 | 23 | yes | 6.6 |  | 18400 |  | Portable AC/Dehumidifier/Heater that can be used in OR and recovery (8000 BTU 250-300 Sq ft)
Recovery Suction | 1 | 120V | 6 | 6 | 720 | 0.25 | no |  | 6 |  | 180 | Turns on Intermittenly for suction.
Recovery Lights | 1 | 120V | 1.3 |  | 160 | 23 | yes | 1.3 |  | 3680 |  | Maximum duration could be 23 hours
Recovery Defibrillator | 1 | 120V | 3.5 | 3.5 | 420 | 0.25 | no |  | 3.5 |  | 105 | Code Blue in Recovery
Recovery Monitor | 1 | 120V | 1.6 | 1.6 | 200 | 23 | yes | 1.6 |  | 4600 | 5947.5 | Blood pressure, SPO2, EKG Monitor
Continuos AMPS | 36.55 |  | 123.2 | 74.15
Continuous Output Power | 4.3 kW
Stand-By AMPS | 40.5
Continuous Stand By Power | 4.9 kW
Maximum Amps | 123.2
OR Settings Maximum Amps | 74.15
Continous Wattage Used 23hr | 32152
Stand By Wattage 23 Hr | 5947.5
Total Watt Consumption in 23HR | 38099.5