CHAPTER 16

GAS SYSTEM

ARTICLE I - DEPARTMENT

16-1-1	DEPARTMENT ESTABLISHED.  There is hereby established a department of the municipal government which shall be known as the Gas Department.  It shall consist of the Gas Committee and the Gas Superintendent.

16-1-2	GAS COMMITTEE.  The City Council standing committee on Gas shall exercise a general supervision over the affairs of the Gas System.  It shall determine the needs thereof and shall, from time to time, report its findings to the Mayor and City Council so that a full understanding thereof shall be had, and generally, shall do all acts necessary to promote the efficiency of the Department.  Prior to the adoption of the appropriation ordinance, the Committee shall prepare and submit an estimate of the receipts and expenditures of the system for the fiscal year.

16-1-3	GAS SUPERINTENDENT.  It shall be the duty of the Gas Superintendent to manage and control all aspects of the Gas System.  He shall recommend to the Committee the needs and conditions of the Gas System.

ARTICLE II - GAS RATES AND FEES

16-2-1 	APPLICATION FOR SERVICE CONNECTIONS.  Any person, firm or corporation desiring to make a gas tap or service connection with the Natural Gas System of the City shall file a written application in the office of the City Clerk.

In the event such application is made by an agent for the owner, then such application shall also be accompanied by the written authority of the owner to the agent for the making of the application.  Where service lines are laid on private property, an easement shall be executed by the owner thereof, providing for the installation and maintenance of the proposed service lines to be installed and maintained by the City and for the extension along or across such property for making other service connections from the same service line.  (Ord. No. 311; 06-04-56)  (See Section 16-2-3(E).)

16-2-2	FEES.  A fee of Two Hundred Dollars ($200.00) shall be paid to the City Collector when any application for gas is made.  The deposit made by the applicant shall be held by the City as security for payment for gas service and may be used as payment when a default in payment occurs.  The deposit shall not be used to earn interest for either the City or the applicant.

16-2-3	GAS RATES.  The rates and charges for the use and services of the municipal gas utility of the City are hereby established.  Such rates and charges shall be made and collected against each consumer who shall directly or indirectly receive gas from the municipal utility.  The rates and charges shall be based upon the quantity of gas used by each consumer, as measured by the gas meter.

The charges shall be computed as follows:

GR1 - Residential/Commercial and GR2 Residential/Commercial (Outside City)

Usage (Per CCF)			Base Amount			Rate for Excess

0-5	$8.99	$1.28

5-15	15.39	1.10

15-35	26.39	1.10

35-100	48.39	1.00

100 and up	113.39	0.96

PLUS - Any and all applicable gas taxes; and

PLUS - A Gas Rate Adjustment equal to: and

The actual average cost per DTH of gas purchased for the prior month by the City of Jonesboro; and

LESS - The base rate of $7.00 per DTH, DIVIDED by ten (10), for each CCF of gas used.

GR3 - Industrial

Usage (Per CCF)			Base Amount			Rate for Excess

0-100	$125.00	$1.20

100-600	245.00	1.10

601 and up	795.00	1.00

PLUS - Any and all applicable gas taxes; and

PLUS - A Gas Rate Adjustment equal to: and

The actual average cost per DTH of gas purchased for the prior month by the City of Jonesboro; and

LESS - The base rate of $7.00 per DTH, DIVIDED by ten (10), for each CCF of gas used.

(Ord. No. 2005-07; 10-17-05)

(A)		The minimum monthly charge for residential and commercial use shall be Eight Dollars ($8.00).

(B)		The minimum monthly charge for industrial use shall be One Hundred Dollars ($100.00).

(C)		Each charge, and each billing therefore shall be subject to any tax imposed on the sale or distribution of natural gas by the City and shall be added to each charge and billing for service by computation of a percentage factor equivalent to the effect of the tax.

(D)		In the event of any change in the cost of acquisition of gas to the City from its supplier, then the City Council of the City may, by Resolution, change the above and foregoing rates and charges to reflect and account for such change in cost, by calculation of a percentage cost factor or unit cost per one hundred (100) cubic feet and applying such cost factor to the above rates and charges, for which purpose the date establishing the base cost of purchased gas is and shall be the same as the effective date of this Article.

(E)		A connection charge of Five Hundred Dollars ($500.00) shall be paid by the user to the Jonesboro Municipal Gas System for each connection inside the corporate limits, and Six Hundred Dollars ($600.00) for each connection outside the corporate limits.  Fee must be paid at time of application for service.  Any additional pipe or fittings used over the allowed one hundred (100) feet per connection, shall be paid for by the user to the City at the same cost of supplier to City before service will be turned on for the user.  (Ord. No. 93-2; 02-01-93)

(F)		Any user outside the corporate limits shall pay a monthly service charge of Two Dollars ($2.00) to cover the cost of billing, bookkeeping, and postage.

All rates and charges shall be non-discriminatory, provided the City Council of the City may impose special rates and charges in cases where particular circumstances render the regular rates unjust, inadequate, or inequitable, and may fix and impose special charges where interrupted service is given.

(G)		The City will supply gas to users only through a meter, which meter will be read monthly by the City.

(H)		Each bill for charges hereunder shall be due on the twentieth (20th) day of the month in which it is rendered, and if any bill is not paid on or before the twentieth (20th) day of said month, said bill is declared delinquent and a ten percent (10%) penalty shall be added to delinquent bill, and if any bill remains delinquent ten (10) days or more, then, such delinquent customer’s service may be disconnected and may not be reconnected except upon the payment of all delinquent bills, together with a ten percent (10%) penalty and a reconnection charge of Five Dollars ($5.00).

(I)		The City’s providing gas service to a particular lot, parcel, or premises, shall deem to be furnished to both the occupant and the owner thereof and it shall be deemed an obligation of both the occupant and owner of any such lot, parcel or premises.  (Ord. No. 80-10; 12-22-80)

(J)		A Five Dollar ($5.00) per month Rate Adjustment Charge shall be added to each customer’s bill.  (Ord. No. 2006-04; 10-16-06)

16-2-4	SPECIAL RATES; NO FREE SERVICE.  No free service of the gas utility shall be furnished to any person, firm, organization, or corporation, public or private, and all rates and charges shall be non-discriminatory, provided that the City Council reserves the right to impose special rates and charges in cases where particular circumstances render the regular rates inadequate or unjust.  If the City should elect to supply itself with gas for any purpose, regular rates therefor shall be charged against the City and payment made from the funds thereof to the Gas Fund.  (Ord. No. 471; 03-03-75)

16-2-5	GAS CONTRACT.  The provisions of Chapter 38 are hereby adopted as part of the Gas Code, the provisions thereof shall be controlling on all applicants for gas service, unless otherwise provided for in this Chapter.

16-2-6	RECEIPT OF FUNDS.  It shall be the duty of the City Treasurer to set up and maintain a proper system of accounts and records separate from all other accounts and records, showing the amount of revenues received from the Gas System and the application of such revenues and all financial transactions in connection therewith.  Such accounts shall annually be audited properly by an independent public accountant as provided by the Illinois Municipal Accounting Act.

ARTICLE III - REGULATIONS

16-3-1	FILING OF APPLIANCE APPLICATION.  Applicant shall file an application for gas with the City Clerk stating the equipment to be connected and shall refile when future equipment is added, showing all equipment installed or proposed.

16-3-2	SPECIFICATIONS FOR REGULAR GAS SERVICE CONNECTIONS.  All gas service connections made to the gas mains of the distribution system of the City shall be substantially as follows:

The connection at the main shall consist of a valved service tee for three-fourths (3/4) inch I D field pipe.  Valve tees shall be welded in a workmanlike manner to the main.  The connection with the service tee shall be made with a black iron street ell, nipple and insulated union.  Service lines shall consist of three-fourths (3/4) inch black iron pipe, coated and wrapped to protect it against corrosion, which shall be laid approximately eighteen (18) inches below the ground surface approximately one (1) foot at or near the building to be serviced and fitted with a three-fourths (3/4) inch black iron stop cock.  Prior to drilling the main for gas service, the aforementioned service line shall be tested at one hundred (100) pounds pressure.  The regulator and meters shall be capable of handling a sufficient volume of gas to serve the needs of the customer.  All materials and construction procedure shall conform to the latest standards of the American Gas Association.

Wherever it is necessary for service lines to cross under high-type pavements, the service line shall be installed by boring or jacking the service line through underneath the pavement from a point six (6) feet outside of the pavement to six (6) feet beyond the edge of the pavement.

All lines and fittings shall be capable of withstanding a working pressure of not less than one hundred twenty-five (125) pounds per square inch and shall be so rated by the manufacturer.  One (1) fitting of the meter swivel shall be insulated.

Service connections, where the gas consumption will be in excess of the capacity of the above specifications, shall be made in the manner specified by the engineer or Superintendent.

16-3-3	ALL SERVICE SHALL BE METERED.  All gas service shall be metered with a meter of adequate size to measure the amount of gas consumed.  Meters shall be of the positive type and shall be American Gas Association approved.

All meters shall be so placed and installed as to render the same accessible at all times for the purpose of reading and repairing.  All meters shall be set outside of the buildings wherever practical.  Indoor installation must be vented with an adequate vent extending to the outside.

16-3-4	METERS OPEN TO INSPECTION.  At all reasonable hours, meters, regulators, fittings fixtures and appurtenances connected with the system and located on private property shall be open to inspection by the proper officers and employees of the City.  Any part found to be defective or not in compliance with the provisions of this Code shall be immediately repaired or corrected.  Service may be discontinued at any time when conditions of the privately owned facilities create danger or a hazard.

16-3-5	METER READING CONCLUSIVE.  All gas customers shall be liable for the gas consumption as shown by the meter.  Waste, leakage, or other causes not the liability of the City, shall be included under the liability.  The meter reading shall be conclusive provided that whenever the City shall find any meter not registering, then an average bill may be rendered based at the option of the City, on either the nearest previous three (3) months average use, when the meter was in good order, or based on the same month or months of the preceding year.  Whenever the City shall have reason to believe that a meter is not registering correctly, then an average bill as stated above may be rendered and the meter removed for testing.  If such average bill should prove to be incorrectly estimated, either by actual testing, or by actual gas consumption, after being replaced by a corrected meter, then such bill shall be compared to the same.

16-3-6	TEST OF METERS.  Any consumer may request the City to make a test of the accuracy of the meter, then in use on their premises.  Such tests will be made by the City without charge, provided that such meter has not been tested within two (2) years preceding such a request.  In case a consumer requests an accuracy test of a meter which has been previously tested within two (2) years, the consumer shall be required prior to making test to deposit with the city the sum of Five Dollars ($5.00), to cover the cost of removing, testing and replacing such meter.

In the event such meter is found by testing, to register incorrectly at full capacity, by more than two percent (2%), then another accurate meter shall be substituted and the test deposit shall be refunded.  Past gas bills shall be adjusted by refund or credit of such percentage of the amount of gas bills for a period of not more than two (2) months previous to such test.

In the event that the meter is found to be registering correctly, the consumer shall forfeit the test deposit and such funds shall be deposited in the gas operating funds of the City.

16-3-7 	SEPARATE METERS FOR EACH DISTINCT PREMISES.  No person, firm or corporation shall connect any gas service pipe or transmit gas supplied by the Natural Gas System of the City into two (2) distinct premises from one (1)

meter.  Apartment buildings having separate dwelling units may be served from a single meter.  Duplex dwellings shall be serviced from individual meters.

16-3-8	CITY NOT LIABLE FOR AN INTERRUPTION OF SERVICE OR SUPPLY.  The City shall have the right to shut off the supply of gas whenever it is necessary to make repairs, improvements, enforce rules or for any operating reason.  In all cases where possible, a reasonable notice of the circumstances will be given to the customers, but in an emergency, the gas may be shut off without notice.  Such necessary repairs or work will be made by the City as rapidly as may be practical.  The City shall not be held responsible or liable because of any shut-off or discontinuance of service for any direct or resultant damages to any person, company or customer.

In the event of such discontinuance of gas service, the City will make every attempt to safeguard the customer and service shall not be renewed until the City authorities have purged the lines and put into service all automatic controls and pilots. The cost of purging of lines, relighting pilots, and checking automatic controls, will be borne by the City and the customer will not be liable.  Where the nature of the customer's operations are not such that an interruption of service might create a hazard or large economic loss, such customer shall provide facilities for standby service, if desired.

Whenever mains, pipes, service connections or other facilities of the gas system are taken up, shut off or interfered with by reasons of any City Street Improvement, the City will endeavor to maintain service so far as is reasonably possible, but will not be directly or indirectly liable for any interruption, poor pressure or damage of any kind either to the customers adjacent to or to other customers affected thereby.  Direct damage to property due to such operations shall be either repaired or replaced by the City without cost to the customer.

The City expressly stipulates with all customers and other persons who may be affected by the discontinuance of service that it will neither insure nor be responsible or liable in any manner for any loss or damages direct or indirect by any reason of any fire, or any other cause and all gas service furnished shall also be conditional upon acts of God, inevitable accidents, fire, strikes, riots, or any other causes.

16-3-9 	CONNECTION WITH PRIVATE LINES - GENERAL RULES AND REGULATIONS.  Whenever a connection is made with a private line, such service shall be metered at the point of such connection and the customer requesting such service shall provide a satisfactory location for the placing of such metering devices, regulators and other materials and equipment required.  Such private lines shall be subject to the inspection and approval of the City prior to making the necessary service connections.

The City shall have the right and option to demand changes, removal or replacement of any pipe, fixtures, or apparatus, which is considered to be faulty, inadequate or hazardous, provided, however, that this provision shall not obligate the City in any way or manner.  The City shall have the right to refuse or to discontinue gas

service without notice to its customers if the City finds any apparatus or appliance in operation which would be detrimental to the efficient operation of the existing facilities.

All persons, firms, corporations and customers are strictly forbidden to attach any electrical ground wire to any fixture or piping which is or may be connected to any gas service pipe, meter or main belonging to the City.  The City will hold the owner of the premises responsible and liable for any damage to its property or injury to the employees of the City caused by such ground wire.  Any and all customers, persons, firms or corporations shall remove any existing ground wires immediately and if such ground wires are not removed after twenty-four (24) hour written notice, the City, through its officials, may enter the property and remove such ground wires and the customer shall pay all costs.  All questions and complaints shall be made to the Gas Department of the City who shall be responsible for the proper investigation.  The Department shall be required to make a full report to the customer in all such cases, a copy of which shall be filed with the City Clerk and reported by him to the City Council at the next regular meeting.  Any disrespectful or unwarranted acts of the City employees shall be reported immediately.  All employees of the City are strictly forbidden to demand or accept any tips, gratuity, or other personal compensation for any services whatsoever rendered during working hours.

16-3-10	REGULATIONS RELATIVE TO CUSTOMER'S PIPING.  All house piping shall be of rigid construction.  The pipe from the outlet of the meter shall be of rigid construction.  The pipe from the outlet of the meter shall be of iron pipe of not less than one (1) inch inside diameter and shall enter the house wall or be securely fastened to the wall by means of suitable metal strap or clamp at a point not more than eighteen (18) inches from the outlet connection of the meter, and if extended along the outside wall shall be fastened to the wall at intervals sufficient to make the piping rigid throughout.  In instances where piping from meter enters the wall, the opposite end shall be securely fastened so that pipe will not turn when fittings at the meter are put on.  The piping from the meter through or along the wall shall constitute, and hereinafter be called the “house pipe manifold”; the one (1) inch manifold will be used where the total hourly demand for gas does not exceed four hundred (400) cubic feet per hour.  Where the total hourly demand of a building or house is in excess of four hundred (400) cubic feet of gas per hour, the City Engineering Department must be consulted for specifications for the house pipe manifold.  (Ord. No. 311; 06-04-56)

From any house pipe manifold, pipe to the various appliances shall be of the same dimensions as the fitting on the appliance where such appliance is designed and approved for natural gas.  Where appliances are to be converted from liquefied petroleum gas, pipe from the manifold to the appliance shall be of such size as would be approved by the American Gas Association for natural gas appliances having the same B.T.U. input rating.

From the house pipe manifold, any appliance pipe may be extended at maximum distance of forty (40) lineal feet.  For each ninety (90) degree turn in the appliance pipe, three (3) lineal feet shall be deducted from the maximum distance.  Copper pipe may be substituted for iron pipe from the manifold to the appliance.  Copper pipe must have O.D. dimension equivalent to I.D. of Standard Iron Pipe.  Only Type K copper pipe may be used.  All copper fittings must be of flare type only.  When copper tubing is used, insulated copper to iron fittings must be used at the meter end and appliance end of the tubing.

No connection will be made with any house type manifold that has not been tested for leakage.

All Gas Conversion Burners to be installed shall be A.G.A. approved, all designed heating plants shall be A.G.A. approved and the manufacturer’s recommendations for the installation shall be followed.

No conversion burner shall be installed in an old or inefficient warm air furnace which is in poor repair or in an old or leaky boiler which is in poor repair.  Test for leakage shall be with oil of Wintergreen or smoke bomb on any warm air heating plant before installing a conversion burner.  Furnaces must be reset if found to be leaking.

Before connecting a flue or vent connector into any chimney, the chimney shall be examined to ascertain that it is properly constructed, clear, clean and will freely conduct the products of combustion from the gas heating appliance in question to the outer air.

All appliances, excepting cook stoves, with over eight thousand (8,000) B.T.U. per hour input rating must be vented.  No unvented appliance excepting cook stoves, shall be placed in the same room with a gas refrigerator.  An approved type vent pipe and draft diverter shall be installed on all gas burning space heating and water heating appliances.  Vent pipe shall be installed with not less than one-half (1/2) inch riser per foot of horizontal run.  General rules for venting as prescribed by A.G.A. must be followed.

All positive type catches on firing door shall be eliminated and a hinge pin and spring be installed.

All heating plants of the down draft type shall be vented by connecting a one (1) inch black iron pipe from the highest point of the flue passage of the heating plant to the flue pipe.  The one (1) inch iron pipe shall be welded or screwed into the furnace in a manner to assure no leakage.

A gas shut-off shall be installed in the fuel line directly above the appliance manifold connection.  Said shut-off to be plainly marked.  Gas pilot line shall be connected to fuel line ahead of Main Shut-off Valve.

A high limit control shall be installed on all heating plants.  A low water cut-off control shall be installed on all gas-fired steam boilers.

All gas burning appliances shall be installed in a location in which the facilities for ventilation permit satisfactory combustion of gas and proper venting under normal conditions of use.  The necessary measures shall be taken to ascertain that the above ventilation conditions are present.

The final tie in of the gas line to the meter shall be made by the City.  Before the final tie is made, it shall be the duty of the City Gas Department to make a complete inspection.

The following bulletins: (1) standards of the National Board of Fire Underwriters for the installation of gas piping and gas appliances in buildings as contained in NBFU No. 54, and (2) American standard installations of gas piping and gas appliances in buildings, bulletin dated 1954, as published by the American Association, Inc., are incorporated herein by reference and made a part hereof, as and to the extent that they had been fully set forth at length herein.

16-3-11 	RULES TO BECOME PART OF CONTRACT.  All the rules and regulations concerning the use of the facilities of the natural gas system of the City and the consumption of gas therefrom shall become a part of the contract with every gas customer, and every gas customer shall be subject thereto and bound thereby.

16-3-12 	EXTENSIONS OF GAS MAINS AND SERVICE.  The City shall not be required to extend service within the City limits, a distance of more than one hundred (100) feet per customer and only then when sufficient funds are available in excess of those required for the proper operation of the system.  Extension of mains and service outside of the City limits shall be subject to approval of the Council and shall also be subject to all of the rules and regulations and provisions as provided herein or as may be amended.

16-3-13	TAMPERING WITH METER.  It shall be unlawful for any person, firm, corporation or customer to break the seal of any meter or in any manner to make any alterations, changes or repairs on the same, or to open any mains, laterals, service pipe, stop cocks, valves or any part thereof or otherwise tamper with or attempt to do any work on either or any of them without authority of the City or its properly authorized agent.  Any person who shall violate any of the provisions of this Section or who shall willfully or maliciously injure or damage any property connected with the Gas System of the City shall be subject to the penalty prescribed by this Code.