IMPORTANT INFORMATION ABOUT YOUR DRINKING WATER

Este informe contiene información muy importante sobre su agua potable.

Tradúzcalo o hable con alguien que lo entienda bien.

- BACTERIOLOGICAL MONITORING REQUIREMENTS NOT MET FOR DEL DIOS MWC

Our water system failed to monitor as required for drinking water standards during the past year and, therefore, was in violation of the regulations. Even though this failure was not an emergency, as our customers, you have a right to know what you should do, what happened, and what we did to correct this situation.

We are required to monitor your drinking water for specific contaminants on a regular basis. Results of regular monitoring are an indicator of whether or not our drinking water meets health standards. During 2022, 2023, and 2024, there were instances when we did not monitor Well 01, Well 02, Well 03, and Well 06 for total coliform and E.coli. Therefore, we cannot be sure of the quality of our drinking water during that time.

What should I do?

- There is nothing you need to do at this time.

- Table 1 on page 2 lists the contaminants we did not properly test for during the last year, how many samples we are required to take and how often, how many samples we took, when samples should have been taken, and the date on which follow-up samples were (or will be) taken.

- If you have health issues concerning the consumption of this water, you may wish to consult your doctor.

What happened?

The DDMWC has worked with the County on all drinking water protocols and policies for more than three decades. With the States more active roll in public drinking water safety and oversight, came  numerous new standards and protocols. Though welcomed, the new requirements created a significant change in operations and policies, and added a lengthy list of requirements that was a little challenging for our small water company. Additionally, the correspondence with the State was occasionally misinterpreted by DDWMC’s superintendent. One of these challenges involved a  difference in County bacteriological testing requirements for raw water sampling and the States requirements.

What is being done to correct the violation?

State required quarterly and monthly raw water bacteriological samples have been adopted into standard operational procedures. Board members will ensure state mandates are met during monthly meetings.

For more information, please contact Roy Dunn at (760) 644-1997

Please share this information with all the other people who drink this water, especially those who may not have received this notice directly (for example, people in apartments, nursing homes, schools, and businesses). You can do this by posting this public notice in a public place or distributing copies by hand or mail.

| TABLE 1: FAILURE TO CONDUCT BACTERIOLOGICAL GROUNDWATER MONITORING |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| ###### Contaminant | Required Sampling Frequency | Number of Samples Required | Number of Samples Collected | When All Samples Should Have Been Taken | When Samples Were Taken |
| ###### Total coliform and E.coli | Quarterly monitoring of Well 01, Well 02, and Well 03 | 3 | 0 | Between April 1 and June 30, 2022 | December 27, 2022 |
|  |  | 3 | 0 | Between July 1 and September 30, 2022 |  |
|  | Monthly monitoring of Well 01, Well 02, Well 03, and Well 06 | 4 | 2 | August 2023 | September 26, 2023 |
|  |  | 4 | 0 | October 2023 | November 28, 2023 |
|  |  | 4 | 2 | October 2024 | Well 03 sampled on November 19, 2024, Well 06 sampled on December 17, 2024 |
|  |  | 4 | 3 | November 2024 | Well 06 sampled on December 17, 2024 |

- REPORTING REQUIREMENTS NOT MET FOR DEL DIOS MWC

Our water system failed to 1) submit disinfectant residual measurements (chlorine concentrations), and 2) submit disinfectant byproduct monitoring reports as required for recordkeeping standards during the past year and, therefore, was in violation of the regulations. Even though this failure was not an emergency, as our customers, you have a right to know what you should do, what happened, and what we did to correct this situation.

What should I do?

- There is nothing you need to do at this time.

- Table 2 on page 3 lists the types of reports we did not submit and/or submitted late, the compliance period, the due date, and submission date.

- If you have health issues concerning the consumption of this water, you may wish to consult your doctor.

| TABLE 2: FAILURE TO SUBMIT REQUIRED REPORTING |  |  |  |
| --- | --- | --- | --- |
| ###### Type | Compliance Period | Due Date | Date of Submission |
| ###### Maximum Residual Disinfectant Level (MRDL) | April 1, 2022 – June 30, 2022 | July 10, 2022 | Never received |
|  | July 1, 2022 – September 30, 2022 | October 10, 2022 | Never received |
|  | October 1, 2022 – December 31, 2022 | January 10, 2023 | January 26, 2023 |
|  | January 1, 2023 – March 31, 2023 | April 10, 2023 | May 7, 2023 |
|  | April 1, 2023 – June 30, 2023 | July 10, 2023 | Never received |
|  | July 1, 2023 – September 30, 2023 | October 10, 2023 | Never received |
|  | October 1, 2023 – December 31, 2023 | January 10, 2024 | Never received |
|  | January 1, 2024 – March 31, 2024 | April 10, 2024 | April 24, 2024 (incomplete) |
|  | April 1, 2024 – June 30, 2024 | July 10, 2024 | August 13, 2024 |
|  | July 1, 2024 – September 30, 2024 | October 10, 2024 | October 20, 2024 |
|  | January 1, 2025 – March 31, 2025 | April 10, 2025 | April 10, 2025 (incomplete) |
|  | April 1, 2024 – June 30, 2025 | July 10, 2025 | July 10, 2025 (incomplete) |
|  | July 1, 2024 – September 30, 2025 | October 10, 2025 | September 29, 2025 (incomplete) |
| ###### Disinfectant Byproduct (DBP) | July 1, 2023 – September 30, 2023 | October 10, 2023 | October 17, 2023 |
|  | October 1, 2023 – December 31, 2023 | January 10, 2024 | Incomplete report submitted on January 11, 2024 |
|  | January 1, 2024 – March 31, 2024 | April 10, 2024 | May 16, 2024 |
|  | April 1, 2024 – June 30, 2024 | July 10, 2024 | August 4, 2024 |
|  | July 1, 2024 – September 30, 2024 | October 10, 2024 | Incomplete report submitted on October 22, 2024 |
|  | October 1, 2024 – December 31, 2024 | January 10, 2025 | January 23, 2025 |
|  | January 1, 2025 – March 31, 2025 | April 10, 2025 | May 1, 2025 |

## What happened?

## As mentioned in an earlier response there was some confusion on sampling protocols. Miscommunication and missed sections of reporting criteria such as proper signatures, dates and inconsistent or improper data logging created some of the late submissions.

## What is being done to correct the violation?

Reports will be reviewed by a second DDMWC employee before submitting to the State, to ensure mistakes or omissions are corrected and reports are turned in on time.

- FAILURE TO CONDUCT GROUNDWATER UNDER DIRECT INFLUENCE OF SURFACE WATER MONITORING AND REPORTING

Groundwater Under the Direct Influence of Surface Water (GWUDI) means any water beneath the surface of the ground with significant occurrence of insects or other macroorganisms, algae or large diameter pathogens such as Giardia lamblia or Cryptosporidium, or significant and relatively rapid shifts in water characteristics such as turbidity, temperature, conductivity, or pH which closely correlate to climatological or surface water conditions.

The concern for surface water influencing Wells 01, 02, and 03 is heightened due to the wells’ proximity to ephemeral and intermittent creeks and substandard construction. In a letter issued to Del Dios on December 27, 2023, the Division instructed Del Dios to implement a GWUDI monitoring plan. The goal of a GWUDI monitoring plan is to determine the wells’ susceptibility to surface water contamination. Paired general physical and bacteriological samples are collected from both groundwater and creek water for comparison.

Our water system failed to conduct GWUDI monitoring between March and September 2024, November and December 2024, and January through September 2025.

What should I do?

- There is nothing you need to do at this time.

## What happened?

## We wrongly assumed that the GWUDI monitoring and reporting criteria was predicated on pooling or running water adjacent to a well and that if there was no pooling or running water in the adjacent creek, we would not be required to monitor or test water from the wells. We have since learned that any active wells within an appreciable distance from a creek would need testing to help establish a baseline for water composition and help determine changes that may indicate surface water intrusion.

## What is being done to correct the violation?

## Better communication with the State regarding well status and addressing State requests or requirements more promptly.

- INITIAL HEXAVALENT CHROMIUM MONITORING REQUIREMENTS NOT MET BY DEL DIOS

Our water system failed to monitor Well 01 and Well 03 for hexavalent chromium by April 1, 2025. Even though this failure was not an emergency, as our customers, you have a right to know what you should do, what happened, and what we did to correct this situation.

What should I do?

- There is nothing you need to do at this time.

- Table 3 below lists the contaminant we did not properly test for during the last year, how many samples we are required to take and how often, how many samples we took, when samples should have been taken, and the date on which follow-up samples were (or will be) taken.

| TABLE 3: FAILURE TO MEET MONITORING DEADLINE |  |  |  |  |
| --- | --- | --- | --- | --- |
| ###### Contaminant | Required Sampling Frequency | Sample Site | When All Samples Should Have Been Taken | When Samples Were or Will Be Taken |
| ###### Hexavalent Chromium | Initial Monitoring must occur between October 1, 2024 and April 1, 2025. | Well 01 | April 1, 2025 | Well 01 has not been monitored. |
|  |  | Well 03 |  | 4/7/2025 |

What happened?

Well 01 has been offline since November of 2024 and there is no plan to restore its operation, for this reason Hexavalent Chromium monitoring was not completed for the State required reporting period.

Well 03 water has not been part the water distribution system for more than 5 years. There is no plan to utilize water from well 03 any time soon.

What is being done to correct the violation?

Better communication with the State on well status and any future changes.

- DIRECTIVES SET FORTH IN DOMESTIC WATER SUPPLY PERMIT NO. 05_14_23P_002 AND PLAN REVIEW LETTER FOR WELL 06 CHLORINATOR NOT MET BY DEL DIOS

The Division of Drinking Water issued Domestic Water Supply Permit No. 05_14_23P_002 to our water system on July 26, 2023. The Division of Drinking Water also issued a review letter for the proposed chlorination system for Well 06 to our water system on March 20, 2025. Our water system failed to comply with 1) five permit conditions included in Domestic Water Supply Permit No. 05_14_23P_002, 2) eight directives included in Domestic Water Supply Permit No. 05_14_23P_002, and 3) nine directives included in the plan review letter for Well 06’s chlorination system.

Even though this failure was not an emergency, as our customers, you have a right to know what you should do, what happened, and what we did to correct this situation.

What should I do?

- There is nothing you need to do at this time.

- Table 4 below lists the permit conditions and directives that our water system did not comply with.

Table 4: SUMMARY OF INCOMPLETE DIRECTIVES

Permit Action Item 7: Complete the distribution datasheet and submit to the Division by October 24, 2023. A template data sheet is included as Enclosure 21. The datasheet includes the following: • Number of (feet) miles of type, size, construction material, age, condition (evaluate number < 4 inches) • Operating pressure (>20 psi). • Water and sewer separation • Construction criteria when separation criteria not met • Program and policy for the replacement of undersized, old or inadequate lines. • Dead ends, number, flush out facilities • Disinfection practices and monitoring for new repaired lines • Valves, number

Permit Action Item 8: Del Dios must submit the 2022 backflow device test certification to the Division by August 23, 2023.

Permit Action Item 11: One hole was found in one vent screen. Del Dios must inspect all four vents and identify if any other holes are present. All vent screens containing holes must be repaired or replaced by September 24, 2023.

Permit Action Item 12: All bird droppings under the vent caps must be removed. Photo documentation of cleaned surface adjacent to vents must be submitted to the Division by August 23, 2023.

Permit Action Item 14: Del Dios must submit the March 2023 tank cleaning/inspection report to the Division by August 23, 2023.

Permit Action Item 17: Del Dios is required to update its Bacteriological Sample Siting Plan (BSSP) to include monthly raw source monitoring of Well 06. Well 06 must also be listed as a triggered source per Groundwater Rule. Del Dios must also specify routine and repeat sample locations for all calendar months. The BSSP must be submitted to the Division by August 23, 2023.

Permit Action Item 18: Del Dios does not have a formal Stage 2 DBPR Compliance Monitoring Plan. Del Dios must submit a DBPR Compliance Monitoring Plan by August 23, 2023.

Permit Action Item 20: Del Dios must submit an emergency chlorination plan for the Division’s review and approval by October 24, 2023.

Permit Condition No. 6: The downhole chlorinators at Wells 01, 02, and 03 must be replaced with Division approved well discharge chlorinators by October 24, 2023.

Permit Condition No. 8: Well 03 must not be used for providing water to the distribution system until Del Dios obtains written approval to place the well back into service. If Del Dios does not have adequate source capacity to meet demands as a result of complying with this condition, contact the Division to discuss additional conditions for operating Well 03. By October 24, 2023, Del Dios must submit a plan to implement water system configuration changes to increase the chlorine contact time in Well 03 to obtain a minimum of 1-log Giardia inactivation with free chlorine, e.g., dedicated transmission line from Well 03 to Storage Tank, or other Division approved plan.

Permit Condition No. 11: Del Dios must complete the following prior to placing Well 06 into service: a. Install a Division approved wellhead discharge chlorination system. The Land-O-Matic™ Dry Pellet Chlorinator (downhole) is not an approved chlorinator for Well 06. Del Dios must propose an alternate disinfection system for Well 06. b. Del Dios must submit Well 06’s Drinking Water Source Assessment (DWSAP) to the Division. c. Install the following surface construction features: - A casing air vent per California Department of Water Resources (DWR) Well Standards, Section 10E. - A non-threaded sample tap, per California Code of Regulations, title 22, section 64560, subsections (c)(3)(E)(2). - A pump to waste discharge line with an air gap, per California Code of Regulations, title 22, section 64560, subsections (c)(3)(F). iv. A “sounding tube” or alternate means of measuring static and dynamic water levels per DWR Well Standards, Section 10A. e. Del Dios must install a Division approved treatment system for the of iron prior to placing into service. Note, a permit amendment must be received prior to installation of any new treatment. g. Monitor Well 06 for total coliform and E.coli using an enumeration method. The results must be reported in units of MPN/100mL. h. Receive written approval from the Division to place the well into service.

Permit Condition No. 23: Del Dios must maintain complete and accurate records to include, but not be limited to, the following information for each valve: • Size and type; • Date installed and maintained; • Function and purpose (main line valve, hydrant branch valve, service line valve, etc.); • Manufacturer (name, model number, etc.); • Position (open or close) in the distribution system; • Direction of operation (right or left) and maximum turns (revolutions) required to open or close the valve completely; • Deficiency and repairs. In addition to the valve records, Del Dios must submit a map that includes all valves in the distribution system to the Division. The valve records and valve map must be submitted to the Division by October 24, 2023.

Permit Condition No. 24: Del Dios must submit a plan for the reduction of TDS from Well 01 & 02 by October 22, 2023. The plan must include a schedule to be approved by the Division.

Well 06 Chlorinator Plan Review Action Item 1: Del Dios must submit a diagram of the proposed chlorination injection point and the location of the proposed chlorine analyzer to the Division by April 19, 2025.

Well 06 Chlorinator Plan Review Action Item 2: Del Dios must provide a description of the storage locations and site security measures for both the chlorine crock and the chlorine stock solution to the Division by April 19, 2025.

Well 06 Chlorinator Plan Review Action Item 3: Del Dios must submit the specifications of the proposed chlorine for Well 06 to the Division by April 19, 2025. The chlorine must be NSF 60 certified.

Well 06 Chlorinator Plan Review Action Item 4: Del Dios must develop an Operation and Maintenance (O&M) Plan to include information about the new wellhead chlorinator. Examples of information that may be included in the O&M are as follows: a. The calculations and protocols for achieving the target influent free chlorine residual concentration in mg/L. b. The target effluent free chlorine residual concentration in mg/L. c. The chlorinator feed rate for achieving target free chlorine residuals. d. All pertinent data recording protocols. e. Frequency and schedule for monitoring chlorine residual at specific locations. f. A completed Disinfection Datasheet must be included. A template is included in Enclosure 24. g. The interval for purchasing chlorine stock solution. The O&M Plan must be submitted to the Division by May 19, 2025.

What happened?

The State required more than 50 items or tasks from the DDMWC. We are a very small water company and needed help addressing some of the States requests. Though additional help was implemented, follow up was not consistent or coordinated well. This led to assumptions and deadline challenges. It should be noted that many of the directives were completed but not submitted for state approval and that none of the incomplete directives affected public health.

What is being done?

Many of the State’s directives are in the process of being completed. Recently, the state approved initial plans for moving forward on the completion of well 06.  The DDMWC is partnering with the California Rural Water Association to help complete the remainder of the State’s mandates.

## Secondary Notification Requirements

Upon receipt of notification from a person operating a public water system, the following notification must be given within 10 days [Health and Safety Code Section 116450(g)]:

- SCHOOLS: Must notify school employees, students, and parents (if the students are minors).

- RESIDENTIAL RENTAL PROPERTY OWNERS OR MANAGERS (including nursing homes and care facilities):  Must notify tenants.

- BUSINESS PROPERTY OWNERS, MANAGERS, OR OPERATORS:  Must notify employees of businesses located on the property.

This notice is being sent to you by Del Dios MWC

State Water System ID#: CA3700866

Date distributed: 12/ 16/2026