## Sheet1
Facility Emeregncy Power Requirements
Equipment | Life Safety | Critical Equipment | Delayed Equipment | Battery Backup | Volts | Amps | Max Watts | Run Watts | Continuous Watts | Comments
Smart Lipo |  |  | √ | √ | 230V | 16A | 3680W | 1610W | 1610W | Settings may be half-strength = 1610 W
Autoclave, Tuttnauer #2540EA |  |  | √ |  | 120V | 11.7A | 1404W | 213W |  | 3 minute "Flash" x 3 OR's [1,404W / 6.6 (9 minues)= 213W
Anesthesia Machine |  | √ |  | √ | 120V | 11.4A | 1368W | 684W |  | Batteries are included beneath work tray.
Multi Parameter Patient Monitor |  | √ |  | √ | 120V | 1.6A | 192W | 192W | 192W | Batteries are included
CO2 Monitor |  | √ |  |  | 120V | 1A | 120W | 120W |  | Batteries may be included when attached to Anesthesia Machine
Scavenger Fan |  | √ |  | √ | 120V | 8.3A | 40W | 40W |  | Batteries may be included.
Bair Hugger |  | √ |  |  | 120V | 9.5A | 1140W | 600W |  | Medium Setting
OR Table |  | √ |  |  | 120V | 2A | 240W | 50W | 50W
Infusion Pump |  |  | √ |  | 120V | 42VA | 75W | 42W |  | Batteries are included. Not necessary;
Suction Pump |  | √ |  |  | 120V | 2.5A | 300W | 150w |  | Suction Pump may be on for 30 minutes out of the hour.
Sequential Compression Device |  | √ |  | √ | 120V | 50VA | 96W | 50W | 50W | Batteries may be included.
Electro Surgical Unit |  | √ |  |  | 120V | 540VA | 540W | 180W | 180W | Used 20 minutes out of the hour. Pen type Bovie. 180W/hr
OR Lights (Duo) | √ | √ |  |  | 120V |  | 160W | 36W | 36W | 18W LED bulbs per Surgical Light
Defibrillator |  | √ |  | √ | 120V | 3.5A | 420W | 360W |  | Batteries are included.
HVAC |  | √ |  |  | 120V |  | 800W | 800W |  | Portable 8000BTU A/C & Dehumidifier
Recovery Suction |  | √ |  |  | 120V | 2.5A | 300W | 150w |  | Suction Pump may be on for 30 minutes out of the hour.
Recovery Lights | √ | √ |  |  | 120V | 1A | 120W | 120W |  | 120W - four overhad flourescent bulbs
Recovery Patient Monitor |  | √ |  | √ | 120V | 1.6A | 192W | 192W | 192W | Battries are included.
Hallway Lights | √ |  |  | √ | 120V | 0 | 0 | 0 |  | Battries are included.
Smoke Detectors | √ |  |  | √ | 120V | 0 | 0 | 0 |  | Battries are included.
Fire Alarms | √ |  |  | √ | 120V | 0 | 0 | 0 |  | Battries are included.
Exit Signs | √ |  |  | √ | 120V | 0 | 0 | 0 |  | Battries are included.
Total Maximum Watts
Total Running Watts
Total Watts for General Anesthesia | [7 empty] | 2,620W
Total Watts for IV Sedation | [8 empty] | 2,310W